33kV Feeder Outage Report — Kaduna Region

Week 3  |  Reporting Period: 13–19 September 2026  |  Scope: TCN-attributed 33kV feeder interruptions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report looks at all 33kV feeder outages caused by TCN (Transmission Company of Nigeria) equipment in Kaduna Region from 13 to 19 September 2026 (Week 3). It checks these outages against the TCN/DISCO Fault Attribution Ratio (30:70), which is the split agreed in the Service Level Agreement (SLA).

Important: this analysis covers only Week 3 (13-19 September), not the full month. If outage durations on the feeders listed below are reduced going forward, TCN's overall default level will improve. These feeders should be monitored closely for the remainder of the month.

Compared with Week 2: outages went from 118 to 49, and estimated cost exposure this week is down from ₦8,948.33 in Week 2 to ₦0.00 in Week 3.

# 1. Executive Summary

| Metric | Value |
| --- | --- |
| Number of Outages | 49 |
| Total Outage Minutes | 4,035.00 |
| Total Outage Hours | 67.25 |
| Average Duration (minutes) | 82.35 |
| Total Load Loss (MWh) | 249.87 |

## 1.1 Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Forced | 63.3% |
| Planned | 36.7% |

Who is responsible: every outage in this report is caused by TCN equipment (33kV feeders on the transmission side). No DISCO-caused outages are included here.

# 2. Top Stations by Outage Minutes

| Station | Outages | Total Min | Avg Min | Total Load Loss (MWh) | Avg Load Loss (MWh) |
| --- | --- | --- | --- | --- | --- |
| Mando 132kV | 21 | 2,415.00 | 115.00 | 208.41 | 9.92 |
| Talata-Mafara 132kV | 20 | 1,332.00 | 66.60 | 21.26 | 1.06 |
| Zaria 132kV | 7 | 275.00 | 39.29 | 19.03 | 2.72 |
| Kaduna Town 132kV | 1 | 13.00 | 13.00 | 1.17 | 1.17 |

# 3. Top Feeders by Outage Hours

| Feeder (Station) | Outages | Total Hrs | Avg Hrs | Total Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| AIRPORT (Mando 132kV) | 8 | 14.93 | 1.87 | 76.01 |
| U/DOSA (Mando 132kV) | 3 | 7.80 | 2.60 | 38.91 |
| RIGASA (Mando 132kV) | 4 | 7.23 | 1.81 | 49.05 |
| JAJI (Mando 132kV) | 2 | 7.20 | 3.60 | 9.81 |
| DOKA (Mando 132kV) | 3 | 7.08 | 2.36 | 59.66 |
| MAFARA (Talata-Mafara 132kV) | 5 | 5.55 | 1.11 | 19.32 |
| MARADUN (Talata-Mafara 132kV) | 5 | 5.55 | 1.11 | 0.56 |
| BAKURA (Talata-Mafara 132kV) | 5 | 5.55 | 1.11 | 0.56 |
| ANKA (Talata-Mafara 132kV) | 5 | 5.55 | 1.11 | 0.83 |
| MOTHER CAT (Mando 132kV) | 2 | 5.22 | 2.61 | 6.50 |

# 4. SLA Compliance — Allowable Outage Hours by Band

Every DISCO band (A, B, C, D) has a set number of hours TCN is allowed to be down; where a station has no recorded DISCO/band, a default of 4 hours/day is assumed. The table below lists feeders where TCN's total outage hours went over that limit, shown as a negative number in the last column.

No feeder in this region went over its band limit during the reporting period.

# 5. TCN Outage-Hour Allocation Exceedance & Estimated Cost

This week, the outage-hour allocation is the same band-based figure used in Section 4 (or the 4 hours/day default where no band is recorded) — so a feeder listed in Section 4 will show up here too, with the same shortfall now expressed as excess hours and cost. The cost below only counts the hours a feeder was down after its allocation ran out, using the actual load recorded during those extra hours.

No feeder in Kaduna Region went over TCN's outage-hour allocation this week. Estimated cost: ₦0.00.

# 6. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_______________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria