33kV Feeder Outage Report — Lagos Region

Week 3  |  Reporting Period: 13–19 September 2026  |  Scope: TCN-attributed 33kV feeder interruptions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report looks at all 33kV feeder outages caused by TCN (Transmission Company of Nigeria) equipment in Lagos Region from 13 to 19 September 2026 (Week 3). It checks these outages against the TCN/DISCO Fault Attribution Ratio (30:70), which is the split agreed in the Service Level Agreement (SLA).

Important: this analysis covers only Week 3 (13-19 September), not the full month. If outage durations on the feeders listed below are reduced going forward, TCN's overall default level will improve. These feeders should be monitored closely for the remainder of the month.

Compared with Week 2: outages went from 570 to 548, and estimated cost exposure this week is up from ₦47,802,685.00 in Week 2 to ₦534,299,209.50 in Week 3.

# 1. Executive Summary

| Metric | Value |
| --- | --- |
| Number of Outages | 548 |
| Total Outage Minutes | 89,204.00 |
| Total Outage Hours | 1,486.73 |
| Average Duration (minutes) | 162.78 |
| Total Load Loss (MWh) | 9,131.08 |

## 1.1 Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Emergency | 88.8% |
| Forced | 5.6% |
| Planned | 5.6% |

Who is responsible: every outage in this report is caused by TCN equipment (33kV feeders on the transmission side). No DISCO-caused outages are included here.

# 2. Top Stations by Outage Minutes

| Station | Outages | Total Min | Avg Min | Total Load Loss (MWh) | Avg Load Loss (MWh) |
| --- | --- | --- | --- | --- | --- |
| Oworonshoki 132kV | 30 | 11,542.00 | 384.73 | 1,114.39 | 37.15 |
| Alimosho 132kV | 63 | 8,328.00 | 132.19 | 530.34 | 8.42 |
| New Abeokuta 132kV | 24 | 7,809.00 | 325.38 | 670.69 | 27.95 |
| Aja 132kV | 14 | 7,334.00 | 523.86 | 965.72 | 68.98 |
| Otta 132kV | 40 | 7,236.00 | 180.90 | 854.62 | 21.37 |
| Abeokuta 132kV | 23 | 5,954.00 | 258.87 | 540.31 | 23.49 |
| Akangba 132kV | 32 | 5,207.00 | 162.72 | 561.08 | 17.53 |
| Alausa 132kV | 30 | 5,086.00 | 169.53 | 554.50 | 18.48 |
| Isolo 132kV | 38 | 4,550.00 | 119.74 | 498.03 | 13.11 |
| Ogba 132kV | 38 | 4,307.00 | 113.34 | 667.76 | 17.57 |

# 3. Top Feeders by Outage Hours

| Feeder (Station) | Outages | Total Hrs | Avg Hrs | Total Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| MOWE (New Abeokuta 132kV) | 8 | 71.18 | 8.90 | 429.55 |
| INDUSTRIAL 33kV (New Abeokuta 132kV) | 10 | 54.43 | 5.44 | 236.01 |
| LAGOS ROAD (Abeokuta 132kV) | 5 | 44.40 | 8.88 | 276.85 |
| ALAPERE (Oworonshoki 132kV) | 6 | 43.20 | 7.20 | 62.13 |
| T6-15MVA 33/11KV (Alausa 132kV) | 14 | 39.30 | 2.81 | 199.81 |
| T6-15MVA 33/11KV (Alimosho 132kV) | 14 | 39.30 | 2.81 | 199.81 |
| T6-15MVA 33/11KV (Agbara 132kV) | 14 | 39.30 | 2.81 | 199.81 |
| OWODE EGBA (Abeokuta 132kV) | 4 | 33.82 | 8.45 | 217.78 |
| IGBOBI (Oworonshoki 132kV) | 5 | 33.77 | 6.75 | 211.65 |
| NEW OWORO (Oworonshoki 132kV) | 5 | 30.33 | 6.07 | 112.42 |

# 4. SLA Compliance — Allowable Outage Hours by Band

Every DISCO band (A, B, C, D) has a set number of hours TCN is allowed to be down; where a station has no recorded DISCO/band, a default of 4 hours/day is assumed. The table below lists feeders where TCN's total outage hours went over that limit, shown as a negative number in the last column.

| Station | Feeder | TCN Hrs | Band Allocation (Hrs) | Available (Hrs) |
| --- | --- | --- | --- | --- |
| New Abeokuta 132kV | MOWE | 71.18 | 16.80 | -54.38 |
| New Abeokuta 132kV | INDUSTRIAL 33kV | 54.43 | 16.80 | -37.63 |
| Oworonshoki 132kV | ALAPERE | 43.20 | 8.40 | -34.80 |
| Abeokuta 132kV | LAGOS ROAD | 44.40 | 16.80 | -27.60 |
| Abeokuta 132kV | OWODE EGBA | 33.82 | 8.40 | -25.42 |
| Oworonshoki 132kV | IGBOBI | 33.77 | 8.40 | -25.37 |
| Oworonshoki 132kV | OGUDU 1 | 29.00 | 8.40 | -20.60 |
| Oworonshoki 132kV | TR1 - 15MVA | 25.37 | 8.40 | -16.97 |
| Isolo 132kV | AJAO | 24.92 | 8.40 | -16.52 |
| Itire 132kV | AGO 1 | 23.72 | 8.40 | -15.32 |
| Alimosho 132kV | EKORO | 21.82 | 8.40 | -13.42 |
| Alausa 132kV | OPIC | 21.45 | 8.40 | -13.05 |
| Akangba 132kV | RANDLE | 20.77 | 8.40 | -12.37 |
| Isolo 132kV | PTC | 20.58 | 8.40 | -12.18 |
| Alimosho 132kV | TOWER | 20.28 | 8.40 | -11.88 |

# 5. TCN Outage-Hour Allocation Exceedance & Estimated Cost

This week, the outage-hour allocation is the same band-based figure used in Section 4 (or the 4 hours/day default where no band is recorded) — so a feeder listed in Section 4 will show up here too, with the same shortfall now expressed as excess hours and cost. The cost below only counts the hours a feeder was down after its allocation ran out, using the actual load recorded during those extra hours.

| FEEDERS OVER ALLOCATION 41 | TOTAL EXCESS HOURS 503.5 hrs | TOTAL EXCESS LOAD LOSS 3,101.12 MWh | ESTIMATED COST ₦534,299,209.50 |
| --- | --- | --- | --- |

| Station | Feeder | TCN Hrs | Allocation (Hrs) | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- | --- |
| Oworonshoki 132kV | OGUDU 1 | 29.00 | 8.40 | 20.60 | 271.64 | ₦56,907,882.00 |
| Oworonshoki 132kV | IGBOBI | 33.77 | 8.40 | 25.37 | 211.65 | ₦44,340,675.00 |
| Abeokuta 132kV | OWODE EGBA | 33.82 | 8.40 | 25.42 | 146.33 | ₦30,655,786.00 |
| Isolo 132kV | AJAO | 24.92 | 8.40 | 16.52 | 136.53 | ₦28,602,337.00 |
| Aja 132kV | MAROKO | 19.10 | 8.40 | 10.70 | 117.70 | ₦24,658,150.00 |
| Itire 132kV | AGO 1 | 23.72 | 8.40 | 15.32 | 108.52 | ₦22,734,591.00 |
| Alausa 132kV | OPIC | 21.45 | 8.40 | 13.05 | 103.46 | ₦21,675,568.00 |
| Oworonshoki 132kV | TR1 - 15MVA | 25.37 | 8.40 | 16.97 | 101.95 | ₦21,357,827.00 |
| Akangba 132kV | RANDLE | 20.77 | 8.40 | 12.37 | 100.81 | ₦21,118,997.00 |
| New Abeokuta 132kV | MOWE | 71.18 | 16.80 | 54.38 | 288.67 | ₦19,398,400.00 |
| Otta 132kV | ESTATE | 18.77 | 8.40 | 10.37 | 88.22 | ₦18,483,138.00 |
| Isolo 132kV | PTC | 20.58 | 8.40 | 12.18 | 83.43 | ₦17,477,887.00 |
| Ejigbo 132kV | OKE-AFA II | 19.38 | 8.40 | 10.98 | 70.03 | ₦14,670,237.00 |
| Alausa 132kV | MAGODO | 16.68 | 8.40 | 8.28 | 67.71 | ₦14,185,943.00 |
| Oworonshoki 132kV | ALAPERE | 43.20 | 8.40 | 34.80 | 62.05 | ₦12,999,545.00 |
| Otta 132kV | IJAGBA | 17.38 | 8.40 | 8.98 | 55.29 | ₦11,583,604.00 |
| Abeokuta 132kV | LAGOS ROAD | 44.40 | 16.80 | 27.60 | 162.12 | ₦10,894,464.00 |
| Alausa 132kV | T6-15MVA 33/11KV | 17.28 | 8.40 | 8.88 | 51.99 | ₦10,891,905.00 |
| New Abeokuta 132kV | INDUSTRIAL 33kV | 54.43 | 16.80 | 37.63 | 159.34 | ₦10,707,760.00 |
| Alimosho 132kV | AGEGE | 18.20 | 8.40 | 9.80 | 50.02 | ₦10,479,190.00 |
| Akangba 132kV | IGANMU-2 | 16.58 | 8.40 | 8.18 | 48.27 | ₦10,111,867.00 |
| Ogba 132kV | PTC-EXPRESS | 12.20 | 8.40 | 3.80 | 46.38 | ₦9,717,308.00 |
| Isolo 132kV | IDI-ARABA | 16.37 | 8.40 | 7.97 | 44.62 | ₦9,347,192.00 |
| Itire 132kV | T3A-15MVA 33/11KV | 20.02 | 8.40 | 11.62 | 43.01 | ₦9,010,595.00 |
| Alimosho 132kV | NEW-GOWON (ADIYAN) | 19.57 | 8.40 | 11.17 | 40.45 | ₦8,474,973.00 |
| Alimosho 132kV | T8-15MVA 33/11KV | 17.33 | 8.40 | 8.93 | 35.36 | ₦7,407,920.00 |
| Ogba 132kV | CISCO | 10.75 | 8.40 | 2.35 | 35.25 | ₦7,384,875.00 |
| Alimosho 132kV | TOWER | 20.28 | 8.40 | 11.88 | 35.24 | ₦7,383,828.00 |
| Otta 132kV | TOLL-GATE | 12.78 | 8.40 | 4.38 | 34.95 | ₦7,322,025.00 |
| Alimosho 132kV | EKORO | 21.82 | 8.40 | 13.42 | 34.73 | ₦7,276,284.00 |
| Otta 132kV | IDIROKO ROAD | 27.47 | 16.80 | 10.67 | 98.10 | ₦6,592,320.00 |
| Odogunyan 132kV | OGIJO | 13.52 | 8.40 | 5.12 | 30.70 | ₦6,431,650.00 |
| Ogba 132kV | ABEOKUTA EXP | 9.68 | 8.40 | 1.28 | 19.89 | ₦4,167,304.00 |
| Oworonshoki 132kV | T2 15MVA | 26.40 | 16.80 | 9.60 | 51.19 | ₦3,194,048.00 |
| Abeokuta 132kV | OWODE II | 11.28 | 8.40 | 2.88 | 7.81 | ₦1,635,497.00 |
| Aja 132kV | ILASAN | 19.08 | 16.80 | 2.28 | 25.12 | ₦1,589,885.00 |
| Ogba 132kV | UNIVERSAL STEEL | 9.85 | 8.40 | 1.45 | 5.80 | ₦1,215,100.00 |
| Oworonshoki 132kV | NEW OWORO | 30.33 | 25.20 | 5.13 | 20.77 | ₦951,113.30 |
| Alausa 132kV | OJODU | 9.02 | 8.40 | 0.62 | 3.95 | ₦826,826.70 |
| Ejigbo 132kV | OKE-AFA I | 8.93 | 8.40 | 0.53 | 1.60 | ₦335,200.00 |
| Ogba 132kV | NEW OJODU | 8.45 | 8.40 | 0.05 | 0.47 | ₦99,512.50 |

These figures are from only one week. The feeders listed above should be watched closely and worked on for the rest of the month — cutting their downtime now will directly improve TCN's default level for the full month.

# 6. Root Cause Notes

These notes come from a feeder-by-feeder review of the underlying interruption log for 13-19 September 2026, so the actual cause behind each outage can be addressed directly.

- Oworonshoki 132kV, a station that was not a major factor in Weeks 1-2, is now Lagos Region's largest single driver. Three distinct issues are mixed together there this week: (1) a TR3-30MVA transformer differential trip, (2) repeated load-shedding due to line limitation, including one event explicitly logged as "non-compliance of 30MW load allocation" by the DISCO, and (3) physical damage to the T2-60MVA transformer's secondary breaker interrupter head, which needs equipment replacement, not just a reset.

# 7. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_______________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria