33kV Feeder Outage Report — Port Harcourt Region

Week 3  |  Reporting Period: 13–19 September 2026  |  Scope: TCN-attributed 33kV feeder interruptions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report looks at all 33kV feeder outages caused by TCN (Transmission Company of Nigeria) equipment in Port Harcourt Region from 13 to 19 September 2026 (Week 3). It checks these outages against the TCN/DISCO Fault Attribution Ratio (30:70), which is the split agreed in the Service Level Agreement (SLA).

Important: this analysis covers only Week 3 (13-19 September), not the full month. If outage durations on the feeders listed below are reduced going forward, TCN's overall default level will improve. These feeders should be monitored closely for the remainder of the month.

Compared with Week 2: outages went from 189 to 200, and estimated cost exposure this week is up from ₦11,567,785.84 in Week 2 to ₦32,496,319.00 in Week 3.

# 1. Executive Summary

| Metric | Value |
| --- | --- |
| Number of Outages | 200 |
| Total Outage Minutes | 23,113.00 |
| Total Outage Hours | 385.22 |
| Average Duration (minutes) | 115.56 |
| Total Load Loss (MWh) | 2,084.72 |

## 1.1 Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Forced | 63.0% |
| Emergency | 25.0% |
| Planned | 12.0% |

Who is responsible: every outage in this report is caused by TCN equipment (33kV feeders on the transmission side). No DISCO-caused outages are included here.

# 2. Top Stations by Outage Minutes

| Station | Outages | Total Min | Avg Min | Total Load Loss (MWh) | Avg Load Loss (MWh) |
| --- | --- | --- | --- | --- | --- |
| PH Main 132kV | 57 | 5,916.00 | 103.79 | 685.06 | 12.02 |
| Owerri 132kV | 37 | 3,426.00 | 92.59 | 253.17 | 6.84 |
| Elelenwon 132kV | 8 | 2,957.00 | 369.62 | 399.46 | 49.93 |
| Rumuosi 132kV | 19 | 2,894.00 | 152.32 | 317.18 | 16.69 |
| Uyo 132kV | 18 | 2,791.00 | 155.06 | 175.64 | 9.76 |
| Ahoada 132kV | 19 | 1,279.00 | 67.32 | 19.34 | 1.02 |
| Yenagoa 132kV | 14 | 1,255.00 | 89.64 | 33.09 | 2.36 |
| PH Town 132kV | 9 | 846.00 | 94.00 | 89.99 | 10.00 |
| Eket 132kV | 8 | 746.00 | 93.25 | 46.51 | 5.81 |
| Ekim 132kV | 5 | 480.00 | 96.00 | 15.84 | 3.17 |

# 3. Top Feeders by Outage Hours

| Feeder (Station) | Outages | Total Hrs | Avg Hrs | Total Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| BORI (Elelenwon 132kV) | 3 | 26.00 | 8.67 | 227.04 |
| UNIPORT (PH Main 132kV) | 11 | 19.67 | 1.79 | 192.57 |
| FEEDER 1(AIRPORT) (PH Main 132kV) | 7 | 18.28 | 2.61 | 93.30 |
| UMUAHIA (Owerri 132kV) | 7 | 16.68 | 2.38 | 57.59 |
| UPTH (Rumuosi 132kV) | 3 | 15.50 | 5.17 | 157.21 |
| AIRPORT (Rumuosi 132kV) | 8 | 14.93 | 1.87 | 76.01 |
| ABAK (Uyo 132kV) | 5 | 13.78 | 2.76 | 59.44 |
| ABAK (Eket 132kV) | 5 | 13.78 | 2.76 | 59.44 |
| IGBO ETCHE (Elelenwon 132kV) | 1 | 13.07 | 13.07 | 96.69 |
| REFINERY 1 (PH Main 132kV) | 9 | 13.02 | 1.45 | 138.82 |

# 4. SLA Compliance — Allowable Outage Hours by Band

Every DISCO band (A, B, C, D) has a set number of hours TCN is allowed to be down; where a station has no recorded DISCO/band, a default of 4 hours/day is assumed. The table below lists feeders where TCN's total outage hours went over that limit, shown as a negative number in the last column.

| Station | Feeder | TCN Hrs | Band Allocation (Hrs) | Available (Hrs) |
| --- | --- | --- | --- | --- |
| PH Main 132kV | REFINERY 1 | 13.02 | 8.40 | -4.62 |
| PH Main 132kV | GOLDEN LILY | 11.55 | 8.40 | -3.15 |
| Rumuosi 132kV | RUMUPERIKON | 11.53 | 8.40 | -3.13 |
| Rumuosi 132kV | AIRPORT | 11.28 | 8.40 | -2.88 |
| PH Main 132kV | UNIPORT | 19.67 | 16.80 | -2.87 |
| Uyo 132kV | IKOT EKPENE FDR 2 (OBOT AKARA) | 11.08 | 8.40 | -2.68 |
| PH Main 132kV | ABULOMA | 10.75 | 8.40 | -2.35 |
| Uyo 132kV | FEEDER 7 | 10.57 | 8.40 | -2.17 |
| PH Main 132kV | FEEDER 1(AIRPORT) | 18.28 | 16.80 | -1.48 |
| Rumuosi 132kV | NTA | 8.92 | 8.40 | -0.52 |
| Owerri 132kV | OWERRI 2 (AIRPORT) | 8.68 | 8.40 | -0.28 |
| Owerri 132kV | OWERRI 3 | 8.68 | 8.40 | -0.28 |

# 5. TCN Outage-Hour Allocation Exceedance & Estimated Cost

This week, the outage-hour allocation is the same band-based figure used in Section 4 (or the 4 hours/day default where no band is recorded) — so a feeder listed in Section 4 will show up here too, with the same shortfall now expressed as excess hours and cost. The cost below only counts the hours a feeder was down after its allocation ran out, using the actual load recorded during those extra hours.

| FEEDERS OVER ALLOCATION 12 | TOTAL EXCESS HOURS 26.4 hrs | TOTAL EXCESS LOAD LOSS 184.87 MWh | ESTIMATED COST ₦32,496,319.00 |
| --- | --- | --- | --- |

| Station | Feeder | TCN Hrs | Allocation (Hrs) | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- | --- |
| PH Main 132kV | REFINERY 1 | 13.02 | 8.40 | 4.62 | 59.12 | ₦12,384,942.00 |
| PH Main 132kV | ABULOMA | 10.75 | 8.40 | 2.35 | 19.66 | ₦4,118,072.00 |
| PH Main 132kV | GOLDEN LILY | 11.55 | 8.40 | 3.15 | 18.20 | ₦3,757,956.00 |
| Rumuosi 132kV | AIRPORT | 11.28 | 8.40 | 2.88 | 15.03 | ₦3,149,134.00 |
| Rumuosi 132kV | RUMUPERIKON | 11.53 | 8.40 | 3.13 | 11.54 | ₦2,416,582.00 |
| PH Main 132kV | UNIPORT | 19.67 | 16.80 | 2.87 | 34.88 | ₦2,403,347.00 |
| Uyo 132kV | IKOT EKPENE FDR 2 (OBOT AKARA) | 11.08 | 8.40 | 2.68 | 8.05 | ₦1,686,475.00 |
| Rumuosi 132kV | NTA | 8.92 | 8.40 | 0.52 | 3.41 | ₦714,395.00 |
| Owerri 132kV | OWERRI 3 | 8.68 | 8.40 | 0.28 | 3.15 | ₦658,877.50 |
| PH Main 132kV | FEEDER 1(AIRPORT) | 18.28 | 16.80 | 1.48 | 9.05 | ₦623,430.20 |
| Owerri 132kV | OWERRI 2 (AIRPORT) | 8.68 | 8.40 | 0.28 | 1.70 | ₦356,150.00 |
| Uyo 132kV | FEEDER 7 | 10.57 | 8.40 | 2.17 | 1.08 | ₦226,958.30 |

These figures are from only one week. The feeders listed above should be watched closely and worked on for the rest of the month — cutting their downtime now will directly improve TCN's default level for the full month.

# 6. Root Cause Notes

These notes come from a feeder-by-feeder review of the underlying interruption log for 13-19 September 2026, so the actual cause behind each outage can be addressed directly.

- The Alaoji-related issue flagged in Weeks 1 and 2 is now fully identified: the great majority of this week's PH Main and Owerri line trips (126 events) trace to repeated tripping of one specific unit, the 2ALJ-TR2 150MVA 330/132/33kV transformer at Alaoji TS, plus recurring trips on the Alaoji-Owerri and Afam-related 132kV lines. This is now a confirmed, named piece of equipment rather than a general station reliability concern, which should make it easier to target for repair.

# 7. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_______________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria