33kV Feeder Outage Report — Shiroro Region

Week 3  |  Reporting Period: 13–19 September 2026  |  Scope: TCN-attributed 33kV feeder interruptions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report looks at all 33kV feeder outages caused by TCN (Transmission Company of Nigeria) equipment in Shiroro Region from 13 to 19 September 2026 (Week 3). It checks these outages against the TCN/DISCO Fault Attribution Ratio (30:70), which is the split agreed in the Service Level Agreement (SLA).

Important: this analysis covers only Week 3 (13-19 September), not the full month. If outage durations on the feeders listed below are reduced going forward, TCN's overall default level will improve. These feeders should be monitored closely for the remainder of the month.

Compared with Week 2: outages went from 105 to 109, and estimated cost exposure this week is up from ₦88,559,590.00 in Week 2 to ₦200,295,572.20 in Week 3.

# 1. Executive Summary

| Metric | Value |
| --- | --- |
| Number of Outages | 109 |
| Total Outage Minutes | 56,460.00 |
| Total Outage Hours | 941.00 |
| Average Duration (minutes) | 517.98 |
| Total Load Loss (MWh) | 2,179.75 |

## 1.1 Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Forced | 94.6% |
| Planned | 3.6% |
| Emergency | 1.8% |

Who is responsible: every outage in this report is caused by TCN equipment (33kV feeders on the transmission side). No DISCO-caused outages are included here.

# 2. Top Stations by Outage Minutes

| Station | Outages | Total Min | Avg Min | Total Load Loss (MWh) | Avg Load Loss (MWh) |
| --- | --- | --- | --- | --- | --- |
| Birnin-Kebbi 132kV | 46 | 50,486.00 | 1,097.52 | 1,964.03 | 42.70 |
| Sokoto 132kV | 43 | 4,862.00 | 113.07 | 159.61 | 3.71 |
| Bida 132kV | 2 | 937.00 | 468.50 | 53.02 | 26.51 |
| Shiroro II TS 132kV | 16 | 155.00 | 9.69 | 1.84 | 0.11 |
| Kontagora 132kV | 2 | 20.00 | 10.00 | 1.25 | 0.62 |

# 3. Top Feeders by Outage Hours

| Feeder (Station) | Outages | Total Hrs | Avg Hrs | Total Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| TAMBUWAL (Birnin-Kebbi 132kV) | 2 | 259.13 | 129.57 | 487.73 |
| ARGUNGU (Birnin-Kebbi 132kV) | 2 | 96.77 | 48.38 | 696.28 |
| GAYA (Birnin-Kebbi 132kV) | 2 | 92.20 | 46.10 | 0.21 |
| LABANA (Birnin-Kebbi 132kV) | 9 | 85.07 | 9.45 | 6.59 |
| FADAMA II (Birnin-Kebbi 132kV) | 12 | 78.22 | 6.52 | 506.81 |
| FADAMA (Birnin-Kebbi 132kV) | 11 | 77.72 | 7.07 | 252.38 |
| UNIVERSITY (Birnin-Kebbi 132kV) | 6 | 77.55 | 12.93 | 6.56 |
| GWANDU (Birnin-Kebbi 132kV) | 2 | 74.78 | 37.39 | 7.48 |
| P/STATION (Sokoto 132kV) | 8 | 16.47 | 2.06 | 86.12 |
| FARFARU (Sokoto 132kV) | 9 | 16.38 | 1.82 | 4.42 |

# 4. SLA Compliance — Allowable Outage Hours by Band

Every DISCO band (A, B, C, D) has a set number of hours TCN is allowed to be down; where a station has no recorded DISCO/band, a default of 4 hours/day is assumed. The table below lists feeders where TCN's total outage hours went over that limit, shown as a negative number in the last column.

| Station | Feeder | TCN Hrs | Band Allocation (Hrs) | Available (Hrs) |
| --- | --- | --- | --- | --- |
| Birnin-Kebbi 132kV | TAMBUWAL | 259.13 | 33.60 | -225.53 |
| Birnin-Kebbi 132kV | LABANA | 85.07 | 8.40 | -76.67 |
| Birnin-Kebbi 132kV | ARGUNGU | 96.77 | 25.20 | -71.57 |
| Birnin-Kebbi 132kV | FADAMA II | 78.22 | 8.40 | -69.82 |
| Birnin-Kebbi 132kV | FADAMA | 77.72 | 8.40 | -69.32 |
| Birnin-Kebbi 132kV | UNIVERSITY | 77.55 | 8.40 | -69.15 |
| Birnin-Kebbi 132kV | GWANDU | 74.78 | 8.40 | -66.38 |
| Birnin-Kebbi 132kV | GAYA | 92.20 | 33.60 | -58.60 |
| Sokoto 132kV | P/STATION | 16.47 | 8.40 | -8.07 |
| Sokoto 132kV | FARFARU | 16.38 | 8.40 | -7.98 |
| Sokoto 132kV | NEW INJECTION | 14.18 | 8.40 | -5.78 |

# 5. TCN Outage-Hour Allocation Exceedance & Estimated Cost

This week, the outage-hour allocation is the same band-based figure used in Section 4 (or the 4 hours/day default where no band is recorded) — so a feeder listed in Section 4 will show up here too, with the same shortfall now expressed as excess hours and cost. The cost below only counts the hours a feeder was down after its allocation ran out, using the actual load recorded during those extra hours.

| FEEDERS OVER ALLOCATION 11 | TOTAL EXCESS HOURS 728.9 hrs | TOTAL EXCESS LOAD LOSS 1,697.77 MWh | ESTIMATED COST ₦200,295,572.20 |
| --- | --- | --- | --- |

| Station | Feeder | TCN Hrs | Allocation (Hrs) | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- | --- |
| Birnin-Kebbi 132kV | FADAMA II | 78.22 | 8.40 | 69.82 | 466.49 | ₦97,730,388.00 |
| Birnin-Kebbi 132kV | FADAMA | 77.72 | 8.40 | 69.32 | 208.70 | ₦43,721,847.00 |
| Birnin-Kebbi 132kV | ARGUNGU | 96.77 | 25.20 | 71.57 | 514.84 | ₦26,308,154.00 |
| Birnin-Kebbi 132kV | TAMBUWAL | 259.13 | 33.60 | 225.53 | 423.89 | ₦15,005,588.00 |
| Sokoto 132kV | P/STATION | 16.47 | 8.40 | 8.07 | 54.52 | ₦11,422,638.00 |
| Birnin-Kebbi 132kV | GWANDU | 74.78 | 8.40 | 66.38 | 6.64 | ₦1,390,731.00 |
| Birnin-Kebbi 132kV | UNIVERSITY | 77.55 | 8.40 | 69.15 | 6.56 | ₦1,374,320.00 |
| Sokoto 132kV | NEW INJECTION | 14.18 | 8.40 | 5.78 | 6.20 | ₦1,297,853.00 |
| Birnin-Kebbi 132kV | LABANA | 85.07 | 8.40 | 76.67 | 5.75 | ₦1,204,555.00 |
| Sokoto 132kV | FARFARU | 16.38 | 8.40 | 7.98 | 3.97 | ₦832,064.20 |
| Birnin-Kebbi 132kV | GAYA | 92.20 | 33.60 | 58.60 | 0.21 | ₦7,434.00 |

These figures are from only one week. The feeders listed above should be watched closely and worked on for the rest of the month — cutting their downtime now will directly improve TCN's default level for the full month.

# 6. Root Cause Notes

These notes come from a feeder-by-feeder review of the underlying interruption log for 13-19 September 2026, so the actual cause behind each outage can be addressed directly.

- Birnin-Kebbi 132kV's TAMBUWAL feeder was down for 236 hours (nearly 10 days, 7-16 September) due to a distance-protection relay operating on a fault detected 198.5km away (Zone 2 reach) — worth checking whether the protection settings on this line are correctly coordinated, since a Zone 2 operation of this length is unusual and may point to a relay/settings issue rather than a fault on the local line section.

- Beyond TAMBUWAL, the rest of Birnin-Kebbi's affected feeders continue to trace to repeated 132kV line trips at Mafara TS (and one at Sokoto TS), consistent with the station's dependence on the Talata-Mafara backfeed while the Kainji-Birnin Kebbi 330kV line remains under force majeure repair.

# 7. Key Intervention / Loss Prevention Action by Operations Department

This section documents corrective action the Operations Department has already taken in response to a finding from this analysis.

Birnin-Kebbi 132kV TS: a misattribution has been identified and correction is already underway with NISO.

- Root cause: the sharp rise in this region's attributed cost, particularly at Birnin-Kebbi 132kV TS, traces back to the collapse of Tower T367 on the 330kV Kainji-Birnin Kebbi line (TCN declared force majeure on the circuit, 2KNJ-BRK1, on 8 September 2026). With that circuit down, Birnin-Kebbi TS has depended on a backfeed from Talata-Mafara TS, which cannot carry the station's full load.

- Finding: because of this reduced-capacity backfeed, TCN and the DISCO had already reached an understanding to leave out (shed) certain feeders at certain periods for the duration of the force majeure. However, this agreed shedding arrangement was not reflected on the 33kV interruption sheet, so the affected feeders continued to be logged as ordinary TCN-caused outages — meaning TCN was still being attributed for outages that were, in fact, part of an agreed, force-majeure-related load management arrangement with the DISCO, not a TCN-caused fault.

- How it was caught: this misattribution was only uncovered through the feeder-level analysis carried out by the Operations Department's Outage Report & Analytics Software.

- Action taken: the Operations Department has engaged the NISO Regional Operations Manager (ROM) for Shiroro Region, under which the Birnin-Kebbi Sub-region falls. It has been agreed that a wholesale correction will be made to the attribution records for the affected feeders from 10 September 2026 to date, to properly reclassify them as force-majeure/agreed-shedding events rather than TCN-attributed outages. This is currently in progress, and NISO Headquarters has also been briefed and is supportive of the correction.

- Effect on this report's figures: the Birnin-Kebbi 132kV figures in Sections 1-5 above may overstate TCN's true attributable exposure for the period from 10 September onward, and should be treated as provisional pending the correction. An updated position will be reflected in the next weekly report or issued as an addendum.

# 8. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_______________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria