33kV Feeder Outage Report — Enugu Region

Week 3  |  Reporting Period: 2026-09-13 to 2026-09-19  |  Scope: TCN-attributed 33kV feeder interruptions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report covers Enugu region for Week 3 (13 to 19 September 2026) and is limited to 33kV feeders where the outage is attributed to TCN equipment. During the period, TCN-attributed outages across the region totaled 93 events and 366.65 hours, with an estimated load loss of 2,038.59 MWh. Note that the previous issued period (Week 2) figures on file are inconsistent (outages field shows 335,110,953.33 and cost shows 0), so a reliable week-on-week comparison cannot be made here; readers should rely on the month-to-date figures rather than comparing single weeks.

# 1. Executive Summary

| NUMBER OF OUTAGES 93 | TOTAL OUTAGE HOURS 366.65 | TOTAL LOAD LOSS 2,038.59 MWh |
| --- | --- | --- |

## 1.1 Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Planned | 53.8% |
| Emergency | 41.9% |
| Forced | 4.3% |

All outages listed in this report are attributed to TCN-owned equipment, principally the 3NSHTR5 (Mob-1) 45MVA and 3NSHTR3 (TR13) 60MVA 132/33kV transformers at Onitsha 132kV station, and the responsibility for the resulting SLA exceedances rests with TCN transformer maintenance and protection teams at that station.

# 2. Top Stations by Outage Minutes

| Station | Outages | Total Min | Avg Min | Total Load Loss (MWh) | Avg Load Loss (MWh) |
| --- | --- | --- | --- | --- | --- |
| Onitsha 132kV | 48 | 20,316.00 | 423.25 | 1,884.75 | 39.27 |
| Abakaliki 132kV | 3 | 600.00 | 200.00 | 75.33 | 25.11 |
| GCM 132kV | 5 | 377.00 | 75.40 | 30.14 | 6.03 |
| Agu Awka 132kV | 14 | 343.00 | 24.50 | 28.19 | 2.01 |
| Oji River 132kV | 10 | 170.00 | 17.00 | 3.36 | 0.34 |
| New-Haven 132kV | 8 | 120.00 | 15.00 | 10.58 | 1.32 |
| UNN Nsukka 132kV | 5 | 73.00 | 14.60 | 6.23 | 1.25 |

# 3. Top Feeders by Outage Hours

| Feeder (Station) | Outages | Total Hrs | Avg Hrs | Total Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| OSSAMALA (Onitsha 132kV) | 7 | 61.48 | 8.78 | 280.89 |
| ARMY BARRACKS (Onitsha 132kV) | 7 | 46.70 | 6.67 | 215.68 |
| CANTONMENT (Onitsha 132kV) | 6 | 43.80 | 7.30 | 227.27 |
| AWADA II (Onitsha 132kV) | 6 | 42.88 | 7.15 | 228.58 |
| UMUNYA (Onitsha 132kV) | 7 | 42.87 | 6.12 | 210.29 |
| OBOSI (Onitsha 132kV) | 7 | 33.70 | 4.81 | 218.28 |
| NNEWI INDUSTRIAL (Onitsha 132kV) | 4 | 31.12 | 7.78 | 262.98 |
| NNEWI (Onitsha 132kV) | 2 | 29.02 | 14.51 | 234.24 |
| JUDDY BOLEMA (Onitsha 132kV) | 2 | 7.03 | 3.52 | 6.54 |
| AFIKPO (Abakaliki 132kV) | 1 | 3.33 | 3.33 | 25.67 |
| T3 15MVA (Abakaliki 132kV) | 1 | 3.33 | 3.33 | 21.67 |
| T4 15 MVA (Abakaliki 132kV) | 1 | 3.33 | 3.33 | 28.00 |
| AGU-AWKA (Agu Awka 132kV) | 4 | 2.27 | 0.57 | 27.50 |
| HARBOUR (GCM 132kV) | 1 | 1.28 | 1.28 | 5.65 |
| E- AMOBI (GCM 132kV) | 1 | 1.27 | 1.27 | 0.89 |
| ATANI (GCM 132kV) | 1 | 1.27 | 1.27 | 20.77 |
| GOLDEN OIL (GCM 132kV) | 1 | 1.25 | 1.25 | 1.25 |
| MILLENIUM CITY (Agu Awka 132kV) | 3 | 1.22 | 0.41 | 0.12 |
| TR4 15MVA (GCM 132kV) | 1 | 1.22 | 1.22 | 1.58 |
| AIRPORT (Agu Awka 132kV) | 3 | 1.17 | 0.39 | 0.46 |

# 4. SLA Compliance — Allowable Outage Hours by Band

Each feeder is allowed a fixed number of outage hours per day depending on its assigned band (A or B); feeders with no recorded band are defaulted to 4 hours per day for the purpose of this calculation. The SLA Compliance table below compares each feeder's actual TCN hours against this allowable figure to determine whether it is within or over its allocation for the period.

| Station | Feeder | Band | TCN Hrs | Allocation (Hrs) | Available (Hrs) |
| --- | --- | --- | --- | --- | --- |
| Onitsha 132kV | OSSAMALA | A | 61.48 | 8.40 | -53.08 |
| Onitsha 132kV | ARMY BARRACKS | A | 46.70 | 8.40 | -38.30 |
| Onitsha 132kV | CANTONMENT | A (assumed) | 43.80 | 8.40 | -35.40 |
| Onitsha 132kV | AWADA II | A | 42.88 | 8.40 | -34.48 |
| Onitsha 132kV | UMUNYA | B | 42.87 | 16.80 | -26.07 |
| Onitsha 132kV | OBOSI | B | 33.70 | 16.80 | -16.90 |
| Onitsha 132kV | NNEWI INDUSTRIAL | B | 31.12 | 16.80 | -14.32 |
| Onitsha 132kV | NNEWI | B | 29.02 | 16.80 | -12.22 |
| Onitsha 132kV | JUDDY BOLEMA | A | 7.03 | 8.40 | 1.37 |
| Abakaliki 132kV | AFIKPO | A | 3.33 | 8.40 | 5.07 |
| Abakaliki 132kV | T4 15 MVA | A | 3.33 | 8.40 | 5.07 |
| Abakaliki 132kV | T3 15MVA | A | 3.33 | 8.40 | 5.07 |
| Agu Awka 132kV | AGU-AWKA | A | 2.27 | 8.40 | 6.13 |
| GCM 132kV | HARBOUR | A | 1.28 | 8.40 | 7.12 |
| GCM 132kV | E- AMOBI | A | 1.27 | 8.40 | 7.13 |
| GCM 132kV | ATANI | A | 1.27 | 8.40 | 7.13 |
| GCM 132kV | GOLDEN OIL | A | 1.25 | 8.40 | 7.15 |
| GCM 132kV | TR4 15MVA | A | 1.22 | 8.40 | 7.18 |
| Agu Awka 132kV | MILLENIUM CITY | A | 1.22 | 8.40 | 7.18 |
| Agu Awka 132kV | AIRPORT | A | 1.17 | 8.40 | 7.23 |
| Oji River 132kV | WATER WORKS | A | 0.63 | 8.40 | 7.77 |
| Oji River 132kV | OJI LOCAL | A | 0.57 | 8.40 | 7.83 |
| Agu Awka 132kV | ROTIC | A (assumed) | 0.55 | 8.40 | 7.85 |
| Oji River 132kV | COCA COLA | A | 0.53 | 8.40 | 7.87 |
| Agu Awka 132kV | OGBOJI | A (assumed) | 0.52 | 8.40 | 7.88 |
| New-Haven 132kV | NEW HAVEN | A | 0.50 | 8.40 | 7.90 |
| New-Haven 132kV | GOVT. HOUSE | A | 0.50 | 8.40 | 7.90 |
| New-Haven 132kV | IND. LAYOUT | A | 0.50 | 8.40 | 7.90 |
| New-Haven 132kV | NEW NNPC | A | 0.50 | 8.40 | 7.90 |
| UNN Nsukka 132kV | SUMAS | A | 0.50 | 8.40 | 7.90 |
| UNN Nsukka 132kV | UNN | A | 0.47 | 8.40 | 7.93 |
| Oji River 132kV | ORUMBA | C | 0.60 | 25.20 | 24.60 |
| Oji River 132kV | ACHI | C | 0.50 | 25.20 | 24.70 |
| UNN Nsukka 132kV | ORBA | C | 0.25 | 25.20 | 24.95 |

# 5. TCN Outage-Hour Allocation Exceedance & Estimated Cost

Excess hours are calculated as the TCN outage hours recorded for each feeder minus its allowable hours under its band (or the 4h/day default where no band is recorded); excess load loss and estimated cost are then derived from that excess hours figure. These figures apply strictly to Week 3 (13 to 19 September 2026) and must not be added to other weekly reports to estimate month-to-date totals; only the month-to-date figures should be used for that purpose.

| FEEDERS OVER ALLOCATION 8 | TOTAL EXCESS HOURS 230.77 hrs | TOTAL EXCESS LOAD LOSS 1,230.89 MWh | ESTIMATED COST ₦191,966,750.00 |
| --- | --- | --- | --- |

| Station | Feeder | Band | TCN Hrs | Allocation (Hrs) | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Onitsha 132kV | OSSAMALA | A | 61.48 | 8.40 | 53.08 | 244.96 | ₦51,319,120.00 |
| Onitsha 132kV | CANTONMENT | A (assumed) | 43.80 | 8.40 | 35.40 | 186.95 | ₦39,166,025.00 |
| Onitsha 132kV | AWADA II | A | 42.88 | 8.40 | 34.48 | 176.51 | ₦36,978,845.00 |
| Onitsha 132kV | ARMY BARRACKS | A | 46.70 | 8.40 | 38.30 | 161.92 | ₦33,922,240.00 |
| Onitsha 132kV | UMUNYA | B | 42.87 | 16.80 | 26.07 | 132.56 | ₦8,801,984.00 |
| Onitsha 132kV | NNEWI INDUSTRIAL | B | 31.12 | 16.80 | 14.32 | 123.29 | ₦8,186,456.00 |
| Onitsha 132kV | NNEWI | B | 29.02 | 16.80 | 12.22 | 102.62 | ₦6,813,968.00 |
| Onitsha 132kV | OBOSI | B | 33.70 | 16.80 | 16.90 | 102.08 | ₦6,778,112.00 |

# 6. Root Cause Notes

These notes come from a feeder-by-feeder review of the underlying interruption log for 2026-09-13 to 2026-09-19, so the actual cause behind each outage can be addressed directly.

OSSAMALA feeder at Onitsha 132kV recorded 53.08 excess hours and an estimated cost of NGN 51,319,120, the highest in the region. Six of its seven logged events were tied to "TRF LIM" on the 3NSHTR5 (Mob-1) 45MVA 132/33/11kV transformer, with remarks stating the feeder was repeatedly opened due to transformer load limitation; one planned event on 15 September also cited work to separate the 3NSHTR5 and 3NSHTR3 (TR13) 60MVA bus sections. This is a single recurring cause across multiple long outages, including one of 16.33 hours and one of 14.23 hours.

CANTONMENT feeder (band assumed as Band A) recorded 35.4 excess hours and NGN 39,166,025 in estimated cost. Four events were due to 3NSHTR5 (Mob-1) load limitation; one Forced-class event on 18 September (5.25 hours) was caused by the 3NSHTR3 (TR13) 60MVA transformer Primary CB tripping on "Tap Changer Bucholz," with remarks noting TCN maintenance crew found water content in the OLTC Buchholz relay and sealed minor leakages. The final event on 19 September again cited 3NSHTR3 (TR13) load limitation, showing the fault has shifted between the two transformers.

AWADA II and ARMY BARRACKS feeders, both also fed from the same Onitsha 132kV transformers, recorded 34.48 and 38.3 excess hours respectively, costing NGN 36,978,845 and NGN 33,922,240. Both show the identical pattern: repeated 3NSHTR5 (Mob-1) load-limitation openings, the same 15 September planned bus-separation event, and the same 18 September Forced outage from the 3NSHTR3 (TR13) Buchholz relay trip described above (water content found, leaks sealed). This confirms the same equipment is behind the bulk of excess cost on four separate feeders fed from this station.

UMUNYA, NNEWI INDUSTRIAL, NNEWI and OBOSI feeders, all at Onitsha 132kV and lower cost impact (NGN 8,801,984 down to NGN 6,778,112), also report outages consistently tied to 3NSHTR5 (Mob-1) load limitation, with OBOSI additionally carrying the 15 September planned bus-separation event. No alternative cause is recorded for any of these feeders; the single shared root cause across all eight top-cost feeders is loading constraint and intermittent fault condition on the Onitsha 132kV 3NSHTR5 (Mob-1) and 3NSHTR3 (TR13) transformers.

# Appendix: Assumptions and Overrides

## Feeders priced as Band A (assumed) -- 3

| Station | Feeder |
| --- | --- |
| Onitsha 132kV | CANTONMENT |
| Agu Awka 132kV | ROTIC |
| Agu Awka 132kV | OGBOJI |

## Feeders with DisCo unknown, excluded from cost -- 0

None this period.

## Allowance overrides applied -- 0

None this period.

# 7. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_________________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria