TCN Network Outage & SLA Exceedance Report

Management Summary — Week 3  |  Reporting Period: 2026-09-13 to 2026-09-19  |  All Regions

This report was generated by the TCN Operations Department Outage Report & Analytics Software.

This report brings together 33kV feeder outage and SLA exceedance data for all ten regions for Week 3 (13 to 19 September 2026), covering both TCN and DisCo attributed outages under the standard 30:70 TCN/DISCO cost split. In this period there were 1,173 outages totaling 3,518.62 hours and 18,087.12 MWh of load loss, with 86 feeders exceeding their Band allocation and an estimated cost of NGN 945,773,732. No previous issued period was supplied for comparison, so this week stands as the baseline figure for subsequent trend tracking.

Weekly figures cannot be straight-line summed to produce the month-to-date total. The actual month-to-date estimated cost is NGN 934,148,189, which is lower than this single week's figure of NGN 945,773,732; naively treating this week as representative or adding further weeks on top would overstate the month's true position, so only the reported month-to-date figure should be used for monthly decisions.

## Network-Wide Outage Cause Distribution

| Cause | Share of Outages (%) |
| --- | --- |
| Emergency | 55.4% |
| Forced | 30.9% |
| Planned | 13.6% |

Emergency outages were the largest network-wide cause of downtime this week at 55.4 percent of share, ahead of Forced at 30.9 percent and Planned at 13.6 percent, indicating that most lost hours came from unplanned operational interventions such as line and transformer load limitations rather than equipment failure or scheduled maintenance.

# 1. Network-Wide Key Performance Indicators (Week 3)

| TOTAL OUTAGES 1173 | TOTAL OUTAGE HOURS 3,518.62 | TOTAL LOAD LOSS 18,087.12 MWh | REGIONS REPORTING 10 |
| --- | --- | --- | --- |

## 1.1 TCN Outage-Hour Allocation Exceedance (30% Fault Attribution Ratio)

Outage hours are allocated per feeder against its Band allocation threshold; hours and load loss beyond that allocation are classed as excess, and the estimated cost is derived by applying the 30:70 TCN/DISCO cost ratio to the excess load loss in MWh for each feeder.

| FEEDERS OVER ALLOCATION 86 | TOTAL EXCESS HOURS 1,186.96 hrs | TOTAL EXCESS LOAD LOSS 5,776.72 MWh | ESTIMATED TOTAL COST EXPOSURE ₦945,773,732.00 |
| --- | --- | --- | --- |

# 2. Region-by-Region Outage Summary (Week 3)

| Region | Outages | Total Hrs | Avg Duration (min) | Load Loss (MWh) |
| --- | --- | --- | --- | --- |
| Lagos | 563 | 1,477.57 | 157.47 | 9,092.86 |
| Shiroro | 111 | 565.87 | 305.87 | 1,277.68 |
| Port-Harcourt | 200 | 385.22 | 115.56 | 2,084.72 |
| Enugu | 93 | 366.65 | 236.55 | 2,038.59 |
| Abuja | 63 | 277.18 | 263.98 | 1,617.99 |
| Osogbo | 67 | 181.33 | 162.39 | 854.19 |
| Benin | 19 | 138.80 | 438.32 | 782.41 |
| Kaduna | 49 | 67.25 | 82.35 | 249.87 |
| Kano | 24 | 55.90 | 139.75 | 83.46 |
| Bauchi | 5 | 2.85 | 34.20 | 5.36 |

# 3. TCN Allowable Outage Duration Exceedance by Region (Week 3)

Eight of the ten regions had at least one feeder exceed its allocation this week; Kaduna and Bauchi recorded no feeder exceedances.

| Region | Feeders Over Allocation | Excess Hours | Excess Load Loss (MWh) | Estimated Cost (₦) |
| --- | --- | --- | --- | --- |
| Lagos | 41 | 492.38 | 3,047.88 | ₦521,498,244.00 |
| Enugu | 8 | 230.77 | 1,230.89 | ₦191,966,750.00 |
| Shiroro | 11 | 353.74 | 795.70 | ₦107,861,817.00 |
| Abuja | 5 | 37.50 | 335.48 | ₦55,907,214.00 |
| Port-Harcourt | 12 | 26.41 | 184.85 | ₦32,549,517.00 |
| Benin | 6 | 34.59 | 162.75 | ₦31,974,075.00 |
| Kano | 2 | 10.64 | 12.64 | ₦2,648,080.00 |
| Osogbo | 1 | 0.93 | 6.53 | ₦1,368,035.00 |

# 4. Top 10 Highest-Cost Feeder Exceedances — Week 3 (All Regions)

Lagos region drove the largest share of this week's cost at NGN 521,498,244 across 41 over-allocated feeders, followed by Enugu at NGN 191,966,750 and Shiroro at NGN 107,861,817, with individual station costs led by Birnin-Kebbi 132kV (FADAMA II, NGN 65,952,695) and Onitsha 132kV (OSSAMALA, NGN 51,319,120).

| Station | Region | Feeder | TCN Hrs | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- | --- |
| Birnin-Kebbi 132kV |  | FADAMA II | 46.62 | 38.22 | 314.81 | ₦65,952,695.00 |
| Onitsha 132kV |  | OSSAMALA | 61.48 | 53.08 | 244.96 | ₦51,319,120.00 |
| Oworonshoki 132kV |  | IGBOBI | 29.55 | 21.15 | 211.65 | ₦44,340,675.00 |
| Oworonshoki 132kV |  | OGUDU 1 | 24.78 | 16.38 | 204.17 | ₦42,773,615.00 |
| Onitsha 132kV |  | CANTONMENT | 43.80 | 35.40 | 186.95 | ₦39,166,025.00 |
| Onitsha 132kV |  | AWADA II | 42.88 | 34.48 | 176.51 | ₦36,978,845.00 |
| Onitsha 132kV |  | ARMY BARRACKS | 46.70 | 38.30 | 161.92 | ₦33,922,240.00 |
| Abeokuta 132kV |  | OWODE EGBA | 33.82 | 25.42 | 146.33 | ₦30,656,135.00 |
| Isolo 132kV |  | AJAO | 24.92 | 16.52 | 136.53 | ₦28,603,035.00 |
| Kubwa 132kV |  | 33KV NIPP FDR | 20.23 | 11.83 | 130.17 | ₦27,270,615.00 |
| Aja 132kV |  | MAROKO | 19.10 | 10.70 | 117.70 | ₦24,658,150.00 |
| Itire 132kV |  | AGO 1 | 23.72 | 15.32 | 108.52 | ₦22,734,940.00 |
| Kukwaba 132kV |  | 33KV FDR L35 | 23.32 | 14.92 | 106.03 | ₦22,213,285.00 |
| Alausa 132kV |  | OPIC | 21.45 | 13.05 | 103.46 | ₦21,674,870.00 |
| Oworonshoki 132kV |  | TR1 - 15MVA | 25.37 | 16.97 | 101.95 | ₦21,358,525.00 |

# 5. Comparative Performance (Issued Periods)

Because this is the first issued period with no prior week or month supplied, fair comparison against earlier periods is not yet possible; once a prior period is available, comparisons should be normalized by allocation hours rather than raw totals, since regions have different Band mixes and period lengths. Within this week alone, Lagos shows the largest internal swing, with Onitsha 132kV station alone (OSSAMALA, CANTONMENT, AWADA II, ARMY BARRACKS) accounting for four of the top seven costed feeders, all driven by the same 3NSHTR5 (Mob-1) 45MVA transformer load limitation.

| Metric | Week 1 | Week 2 | Week 3 |
| --- | --- | --- | --- |
| Total Outages | 487 | 1,348 | 1,173 |
| Total Outage Hours | 1,033.87 | 3,304.1 | 3,518.62 |
| Estimated Cost | 315,327,324.08 | 513,847,028.33 | 945,773,732.0 |

## 5.1 Exceedance Cost by Region (Issued Periods)

| Region | Week 1 | Week 2 | Week 3 |
| --- | --- | --- | --- |
| Abuja | ₦0.00 | ₦0.00 |  |
| Bauchi | ₦0.00 | ₦0.00 |  |
| Benin | ₦0.00 | ₦0.00 |  |
| Enugu | ₦0.00 | ₦0.00 | ₦945,773,732.00 |
| Kaduna | ₦0.00 | ₦0.00 |  |
| Kano | ₦0.00 | ₦0.00 |  |
| Lagos | ₦0.00 | ₦0.00 |  |
| Osogbo | ₦0.00 | ₦0.00 |  |
| Port Harcourt | ₦0.00 | ₦0.00 |  |
| Shiroro | ₦0.00 | ₦0.00 |  |

# 6. Aggregate Performance — Month to Date

Section 6 holds the correct combined picture for the month, calculated as one continuous period, not the sum of weeks.

| FEEDERS OVER ALLOCATION (MTD) 54 | ESTIMATED TOTAL COST ₦934,148,189.00 |
| --- | --- |

## 6.3 Top 10 Highest-Cost Feeders — Month-to-Date Cumulative

| Station | Feeder | MTD TCN Hrs | Excess Hrs | Excess Loss (MWh) | Est. Cost (₦) |
| --- | --- | --- | --- | --- | --- |
| Onitsha 132kV | AWADA II | 129.48 | 106.68 | 641.65 | ₦134,425,675.00 |
| Birnin-Kebbi 132kV | FADAMA II | 114.93 | 92.13 | 515.71 | ₦108,041,245.00 |
| Onitsha 132kV | CANTONMENT | 124.03 | 101.23 | 503.41 | ₦105,464,395.00 |
| Onitsha 132kV | ARMY BARRACKS | 132.12 | 109.32 | 501.00 | ₦104,959,500.00 |
| Onitsha 132kV | OSSAMALA | 84.37 | 61.57 | 281.22 | ₦58,915,590.00 |
| Birnin-Kebbi 132kV | FADAMA | 113.80 | 91.00 | 258.40 | ₦54,134,800.00 |
| Oworonshoki 132kV | IGBOBI | 34.23 | 11.43 | 174.35 | ₦36,526,325.00 |
| Sokoto 132kV | P/STATION | 51.22 | 28.42 | 154.39 | ₦32,344,705.00 |
| Onitsha 132kV | NNEWI | 129.23 | 83.63 | 357.69 | ₦23,750,616.00 |
| Birnin-Kebbi 132kV | ARGUNGU | 124.15 | 55.75 | 400.96 | ₦20,489,056.00 |

# 7. TCN Feeders Currently Open (Not Yet Restored)

These TCN-attributed outages have no restoration date or time logged at all, so they cannot be priced or counted as a finished outage -- kept for the record, not included in any figure above.

| Region | Station | Feeder | Opened | Days Open | Class | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Benin | Ihovbor 132kV | EGBA | 2026-09-01 10:12:00 | 33 | Planned | To be patrolled. |
| Benin | Ihovbor 132kV | IHOVBOR | 2026-09-01 10:14:00 | 33 | Planned | Open on WP no. #91686 to enable tcn maintennce crew carry out upgrading of bay equipment of 100MVA transformer, its secondary CB & isolators,primary lighting arreaters and bus setional CB |
| Benin | Ihovbor 132kV | OLUKU | 2026-09-01 09:13:00 | 33 | Planned | Open on WP no. #91686 to enable tcn maintennce crew carry out upgrading of bay equipment of 100MVA transformer, its secondary CB & isolators,primary lighting arreaters and bus setional CB |
| Abuja | Apo 132kV | 33KV FDR H31 | 2026-09-08 19:37:00 | 26 | Forced | DUE TO TRIPPING OF 100MVA 3APHTR4, WHOSE PRIMARY CB TRIPPED ON REF WHILE SECONDARY CB TRIPPED ON GEN TRIP. PHYSICAL INSPECTION REVEALED BLUE PHASE INTERRUPTER HEAD ON PRIMARY BUSHING DETACHED. |
| Abuja | Apo 132kV | 33KV FDR H35 | 2026-09-08 19:37:00 | 26 | Forced | DUE TO TRIPPING OF 100MVA 3APHTR4, WHOSE PRIMARY CB TRIPPED ON REF WHILE SECONDARY CB TRIPPED ON GEN TRIP. PHYSICAL INSPECTION REVEALED BLUE PHASE INTERRUPTER HEAD ON PRIMARY BUSHING DETACHED. |
| Abuja | Apo 132kV | 33KV FDR H37 | 2026-09-08 19:37:00 | 26 | Forced | DUE TO TRIPPING OF 100MVA 3APHTR4, WHOSE PRIMARY CB TRIPPED ON REF WHILE SECONDARY CB TRIPPED ON GEN TRIP. PHYSICAL INSPECTION REVEALED BLUE PHASE INTERRUPTER HEAD ON PRIMARY BUSHING DETACHED. |
| Lagos | Papalanto 132kV | PURECHEM | 2026-09-09 19:42:00 | 25 | Emergency | OPENED ON EMERGENCY DUE TO SERIOUS GLOWING WITH SMOKE OBSERVED ON THE LINE CT CABLE LUG (Yph) |
| Lagos | Akoka 132kV | SABO | 2026-09-13 18:18:00 | 21 | Emergency | OPENED BY CONTROL ON LOAD SHEDDING DUE TO LINE LIMITATION. |
| Lagos | Alagbon 132kV | ADEMOLA 3 | 2026-09-13 18:22:00 | 21 | Emergency | DUE TO LINE LIMITATION |
| Lagos | Alagbon 132kV | KEFFI | 2026-09-13 18:24:00 | 21 | Emergency | DUE TO LINE LIMITATION |
| Lagos | Alagbon 132kV | ALAGBON 1 LOCAL 1 | 2026-09-13 19:03:00 | 21 | Emergency | DUE TO LINE LIMITATION |
| Lagos | Ejigbo 132kV | IJEGUN | 2026-09-13 16:23:00 | 21 | Emergency | FDR OPENED ON LINE LIMITATION |
| Shiroro | Bida 132kV | Al-Hassin Company | 2026-09-15 11:50:00 | 19 | Planned | 3BDA-TR2 WAS OUT OF SERVICE ON W&TP #45867 ISSUED TO ENGR. OLOFIN B.B MGR PC&M-JEBBA ACC TO ENABLE HIM AND HIS TEAM CARRY OUT ANNUAL PREVENTIVE MAINTENANCE. WORK DONE: IR TEST, RATIO TEST, SHORT CIRCU |
| Abuja | Karu 132kV | 33KV FDR K2 | 2026-09-15 22:31:00 | 19 | Emergency | OPENED DUE TO LINE LIMITATION |
| Lagos | Papalanto 132kV | OTA INDUSTRIAL | 2026-09-16 08:36:00 | 18 | Emergency | System load shedding due to 330kv line limitation |
| Lagos | Otta 132kV | IDIROKO ROAD | 2026-09-18 23:08:00 | 16 | Emergency | opened on load shedding due to 330kv line limitation |
| Lagos | Abeokuta 132kV | LAGOS ROAD | 2026-09-19 06:04:00 | 15 | Emergency | opened on load shedding due to 330kv line limitation |
| Lagos | Otta 132kV | IDIROKO ROAD | 2026-09-19 18:16:00 | 15 | Emergency | opened on load shedding due to 330kv line limitation |
| Lagos | Oworonshoki 132kV | NEW OWORO | 2026-09-19 22:11:00 | 15 | Emergency |  |
| Lagos | Papalanto 132kV | ILARO | 2026-09-19 17:01:00 | 15 | Emergency | opened on load shedding due to 330kv line limitation |
| Lagos | Papalanto 132kV | YEWA | 2026-09-19 18:35:00 | 15 | Emergency | opened on load shedding due to 330kv line limitation |

# 8. Key Observations

Birnin-Kebbi 132kV / FADAMA II: 38.2 excess hours, ₦65,952,695.00.

Onitsha 132kV / OSSAMALA: 53.1 excess hours, ₦51,319,120.00.

Oworonshoki 132kV / IGBOBI: 21.1 excess hours, ₦44,340,675.00.

Oworonshoki 132kV / OGUDU 1: 16.4 excess hours, ₦42,773,615.00.

Onitsha 132kV / CANTONMENT: 35.4 excess hours, ₦39,166,025.00.

# 9. Recommendations

Investigate Birnin-Kebbi 132kV / FADAMA II, the largest cost exposure this period.

Investigate Onitsha 132kV / OSSAMALA, the largest cost exposure this period.

Investigate Oworonshoki 132kV / IGBOBI, the largest cost exposure this period.

Section 6 holds the accurate month-to-date picture. Section 2 covers all outages whatever the party; Sections 3, 4 and 6 cover TCN-caused outages only.

# Appendix: Assumptions and Overrides

## Feeders priced as Band A (assumed) -- 23

| Station | Feeder |
| --- | --- |
| Onitsha 132kV | CANTONMENT |
| Kukwaba 132kV | 33KV FDR L35 |
| Isolo 132kV | IDI-ARABA |
| PH Main 132kV | GOLDEN LILY |
| Papalanto 132kV | YEWA |
| Ganmo 132kV | KAM WIRE 33kV |
| Aja 132kV | NTDA 2 |
| Lekki 132kV | MAIYEGUN |
| Ayede 132kV | ELEYELE 33kV |
| Ile-Ife 132kV | OAU |
| Oshogbo 132kV | PRISM 33kV |
| Kukwaba 132kV | 33KV FDR L33 |
| Papalanto 132kV | PURECHEM |
| Maryland 132kV | RACK CENTRE |
| Irrua 132kV | EKPOMA |
| Lekki 132kV | CHEVY VIEW |
| New Abeokuta 132kV | FUNAAB |
| Ojo 132kV | FESTAC 3 |
| Katampe2 132kV | 33kV WUSE II RELIEF FDR |
| Agu Awka 132kV | ROTIC |
| Akure 132kV | FMPI |
| Agu Awka 132kV | OGBOJI |
| Alagbon 132kV | KEFFI |

## Feeders with DisCo unknown, excluded from cost -- 0

None this period.

## Allowance overrides applied -- 0

None this period.

# 10. Approval

This report was reviewed and is hereby submitted for Management's consideration.

_________________________________

Engr. G. A. Aguiyi

General Manager (Operations)

Transmission Company of Nigeria